## Scenario Summary
Costs without carbon pricing | Scenario
| 1 Coal Refurb | 2 Gas-CC + Renew | 3 Gas-CC + Renew | 4 Gas-SC + Renew
Cost of Gas Plant | - | $1.7B for 370 MW | $2.5B for 370 MW | $680M for 250 MW
Gas price ($/GJ) |  | 3 | 8 | 3
Capital + O&M | 11.4 | 12.2098 | 15.4098 | 11.0578
Fuel | 13 | 3.3682 | 8.9819 | 3.9772
Transmission | 1.4 | 1.4 | 1.4 | 1.4
Total | 25.8 | 16.978 | 25.7917 | 16.4351
Cost relative to coal refurbishment | 100% | 65.81% | 99.97% | 63.7%
Savings relative to coal ($B) | 0 | 8.822 | 0.0082819 | 9.3649
Savings per year ($M) | 0 | 367.5826 | 0.34508 | 390.2054
Electricity total (GWh) | 286671 | 286671 | 286671 | 286671
Average cost ($/MWh) | 89.9986 | 59.2247 | 89.9697 | 57.3308
Average cost (cents/kWh) | 8.9999 | 5.9225 | 8.997 | 5.7331
Costs with carbon pricing and OBPS for coal set at 370 tonnes/GWh 2030-2049
GHG total (Mt CO2) | 309.6047 | 54.5737 | 54.5737 | 64.4411
Carbon pricing cost (2026 - 2050 cumulative) | 20.8447 | 5.4064 | 5.4064 | 6.494
Total cost with federal carbon pricing | 46.6447 | 22.3844 | 31.1981 | 22.9291
Cost relative to coal refurbishment | 100% | 47.99% | 66.88% | 49.16%
Savings relative to coal ($B) | 0 | 24.2603 | 15.4466 | 23.7156
Savings per year ($M) | 0 | 1010.8443 | 643.6068 | 988.1505
Average cost with carbon pricing ($/MWh) | 162.7116 | 78.0841 | 108.8291 | 79.984
Average cost with carbon pricing (cents/kwh) | 16.2712 | 7.8084 | 10.8829 | 7.9984
Costs with carbon pricing if OBPS set to 0 tonnes/GWh 2031-2049
Carbon pricing cost (2026 - 2049 cumulative) | 28.5394 | 5.4064 | 5.4064 | 6.494
Total cost with federal carbon pricing | 54.3394 | 22.3844 | 31.1981 | 22.9291
Cost relative to coal refurbishment | 100% | 41.19% | 57.41% | 42.2%
Savings relative to coal ($B) | 0 | 31.9549 | 23.1412 | 31.4103
Savings per year ($M) | 0 | 1331.456 | 964.2185 | 1308.7623
Average cost with carbon pricing ($/MWh) | 189.5531 | 78.0841 | 108.8291 | 79.984
Average cost with carbon pricing (cents/kwh) | 18.9553 | 7.8084 | 10.8829 | 7.9984

## Scenario calculation
Scenario 1 - Keep coal running |  | Scenario 2 - Gas + Renewables | [5 empty] | Scenario 3 - Gas + Renewables (Gas @ $8/GJ, 370 MW @ $2.5B) | [5 empty] | Scenario 4 - Simple Cycle Gas + Extra Renewables (Gas @ $3/GJ, 250 MW @ $680M)
| Coal | Gas | Wind | Solar | Total |  |  | Gas | Wind | Solar | Total |  |  | Gas | Wind | Solar | Total
Capacity (MW) | 1540 | 1480 | 1200 | 300 |  |  |  | 1480 | 1200 | 300 |  |  |  | 1500 | 1500 | 600
Capital cost ($/kw) | 7402.5974 | 4594.5946 | 1900 | 2000 |  |  |  | 6756.7568 | 1900 | 2000 |  |  |  | 2720 | 1900 | 2000
Capital cost ($B) | 11.4 | 6.8 | 2.28 | 0.6 | 9.68 |  |  | 10 | 2.28 | 0.6 | 12.88 |  |  | 4.08 | 2.85 | 1.2 | 8.13
Fixed O&M ($B) | (Assume it is in the $11.4B) | 0.76335 | 0.66924 | 0.28899 | 1.7216 |  |  | 0.76335 | 0.66924 | 0.28899 | 1.7216 |  |  | 0.77366 | 0.83655 | 0.57798 | 2.1882
Fuel cost ($B) | 13 | 3.3682 | 0 | 0 | 3.3682 |  |  | 8.9819 | 0 | 0 | 8.9819 |  |  | 3.9772 | 0 | 0 | 3.9772
Variable O&M cost ($B) | (Assume it is in the $11.4B and $13.0B) | 0.80822 | 0 | 0 | 0.80822 |  |  | 0.80822 | 0 | 0 | 0.80822 |  |  | 0.73966 | 0 | 0 | 0.73966
Transmission cost ($B) | 1.4 | 1.4 |  |  | 1.4 |  |  | 1.4 |  |  | 1.4 |  |  | 1.4 |  |  | 1.4
Fixed O&M ($/MW/year) |  | 20631 | 22308 | 38532 |  |  |  | 20631 | 22308 | 38532 |  |  |  | 20631 | 22308 | 38532
Fleet fixed O&M per year |  | 30533880 | 26769600 | 11559600 |  |  |  | 30533880 | 26769600 | 11559600 |  |  |  | 30946500 | 33462000 | 23119200
Capacity factor | 85% | 51.96% | 40% | 20% |  |  |  | 51.96% | 40% | 20% |  |  |  | 39.27% | 40% | 20%
MWh/year generated per MW | 7446 | 4551.6486 | 3504 | 1752 |  |  |  | 4551.6486 | 3504 | 1752 |  |  |  | 3439.76 | 3504 | 1752
MWh generated by fleet per year | 11466840 | 6736440 | 4204800 | 525600 |  |  |  | 6736440 | 4204800 | 525600 |  |  |  | 5159640 | 5256000 | 1051200
GWh generatedby fleet per year (GWh) | 11466.84 | 6736.44 | 4204.8 | 525.6 |  |  |  | 6736.44 | 4204.8 | 525.6 |  |  |  | 5159.64 | 5256 | 1051.2
Variable O&M ($/MWh) |  | 4.7991 | [5 empty] | 4.7991 | [5 empty] | 5.7342
Variable O&M ($/year) |  | 32328842.4676 | [5 empty] | 32328842.4676 | [5 empty] | 29586237.4199
Fuel efficiency | 30% | 54% | - | - |  |  |  | 54% | - | - |  |  |  | 35.03% | - | -
Fuel used (MWh) per year per MW | 24820 | 8428.979 | [5 empty] | 8428.979 | [5 empty] | 9820.3025
Fuel used (MWh) by fleet per year | 38222800 | 12474888.8889 | [5 empty] | 12474888.8889 | [5 empty] | 14730453.7037
MWh to GJ conversion | 3.6 | 3.6 | [5 empty] | 3.6 | [5 empty] | 3.6
Fuel used (GJ) per year | 137602080 | 44909600 | [5 empty] | 44909600 | [5 empty] | 53029633.3333
GJ to m3 conversion (heat rate 0.03950 GJ/m3) |  | 0.0395 | [5 empty] | 0.0395 | [5 empty] | 0.0395
Natural gas used (m3) per year |  | 1136951898.7342 | [5 empty] | 1136951898.7342 | [5 empty] | 1342522362.8692
Lifetime | 25 | 25 | 25 | 25 |  |  |  | 25 | 25 | 25 |  |  |  | 25 | 25 | 25
Fuel used for 25 years (GJ) | 3440052000 | 1122740000 | [5 empty] | 1122740000 | [5 empty] | 1325740833.3333
Fuel used for 25 years (m3) |  | 28423797468.3544 | [5 empty] | 28423797468.3544 | [5 empty] | 33563059071.73
Fuel cost ($/GJ) | 3.779 | 3 | [5 empty] | 8 | [5 empty] | 3
MWh generated over the lifetime (MWh) | 286671000 | 168411000 | 105120000 | 13140000 | 286671000 |  |  | 168411000 | 105120000 | 13140000 | 286671000 |  |  | 128991000 | 131400000 | 26280000 | 286671000
GWh generated over the lifetime (GWh) | 286671 | 168411 | 105120 | 13140 | 286671 |  |  | 168411 | 105120 | 13140 | 286671 |  |  | 128991 | 131400 | 26280 | 286671
Total cost ($B) | 25.8 |  |  |  | 16.978 | 8.822 | $B cheaper |  |  |  | 25.7917 | 0.0082819 | $B cheaper |  |  |  | 16.4351 | 9.3649 | $B cheaper
Levelized cost ($/MWh) | 89.9986 |  |  |  | 59.2247 | 65.81% |  |  |  |  | 89.9697 | 99.97% |  |  |  |  | 57.3308 | 63.7%
[6 empty] | 8821981.9383 | [13 empty] | Emissions in gas
Emissions intensity of natural gas (g CO2/m3) |  | 1920 | [5 empty] | 1920 | [5 empty] | 1920 | [5 empty] | https://www.canada.ca/en/environment-climate-change/services/climate-change/pricing-pollution-how-it-will-work/output-based-pricing-system/federal-greenhouse-gas-offset-system/emission-factors-reference-values.html
Emissions from gas (tonnes CO2) |  | 54573691.1392 |  |  | 54573691.1392 |  |  | 54573691.1392 |  |  | 54573691.1392 |  |  | 64441073.4177 |  |  | 64441073.4177
Emissions intensity (tonnes CO2/GWh) | 1080 | 324.0506 | 0 | 0 | 190.3705 |  |  | 324.0506 | 0 | 0 | 190.3705 |  |  | 499.5781 | 0 | 0 | 224.791
GHG emissions (Mt CO2) | 309.6047 | 54.5737 | 0 | 0 |  |  |  | 54.5737 | 0 | 0 |  |  |  | 64.4411 | 0 | 0
Annual emissions (Mt CO2) | 12.3842 | 2.1829 | 0 | 0 | 2.1829 | Mt/year |  | 2.1829 | 0 | 0 | 2.1829 | Mt/year |  | 2.5776 | 0 | 0 | 2.5776 | Mt/year
Emissions cost ($B) over lifetime | 20.8447 | 5.4064 |  |  | 5.4064 | $B/year carbon charge |  | 5.4064 |  |  | 5.4064 | $B/year carbon charge |  | 6.494 |  |  | 6.494 | $B/year carbon charge
Total cost ($B) with carbon costs | 46.6447 |  |  |  | 22.3844 | [5 empty] | 31.1981 | [5 empty] | 22.9291
[5 empty] | 47.99% | [5 empty] | 66.88% | [5 empty] | 49.16%
[8 empty] | 8760 | Running 100% capacity factor
[8 empty] | 2838.6835 | tonnes of CO2
[8 empty] | 1474.9646 | Running 52% capacity factor tonnes of CO2
51.96%
[8 empty] | 168.375 | tonnes/GWh effectively
[8 empty] | 65 | regulated limit
[8 empty] | 20.06% | regulated capacity factor

## Capital Cost of Projects
Name | Technology | Location | Cost ($Millions) | Capacity (MW) | Year Commissioned | $/kw | Link
Great Plains Power Station | Gas Combined Cycle (Gas CC) | Moose Jaw | 825 | 377 | 2024 | 2188.3289 | https://www.theglobeandmail.com/business/article-as-construction-of-first-small-modular-reactor-looms-prospective/?login=true
Aspen Power Plant | Gas Combined Cycle (Gas CC) | Lanigan | 1700 | 370 | 2026 | 4594.5946 | https://www.theglobeandmail.com/business/article-saskatchewan-budgets-900-million-to-refurbish-coal-plants-says-no-gas/
Bekevar Wind Farm | Wind | North of Moose Mountain Park | 380 | 200 | 2024 | 1900 | https://www.sasktoday.ca/southeast/local-news/grand-opening-held-for-bekevar-yotin-wind-project-9859841
Iyuhána Solar facility | Solar | Estevan | 200 | 100 | 2026 | 2000 | https://tribalbusinessnews.com/sections/energy/14587-first-nations-community-launches-200m-solar-project-that-will-be-one-of-canada-s-largest
Brandon gas plants | Simple cycle gas plants | Brandon MB | 1360 | 500 | 2030 | 2720 | https://www.pubmanitoba.ca/v1/proceedings-decisions/orders/pubs/26-orders/43-26-revised.pdf
SaskPower coal refurbishment | Coal fired power plants | Estevan and Coronach | 25800 | 1540 | 2026-2035 |  | https://www.cbc.ca/news/canada/saskatchewan/sask-saskpower-coal-refurbishment-9.7198807
680
Unit | Technology | Location | Cost ($Millions) | Capacity (MW) | In service | $/kilowatt | Unit Rebuild Year | Age
BD6 | Coal | Estevan | 327 | 284 | 1977 | 1151.4085 | 2030 | 49 | https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
PR2 | Coal | Coronach | 336 | 291 | 1983 | 1154.6392 | 2031 | 43 | https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
PR1 | Coal | Coronach | 356 | 291 | 1981 | 1223.3677 | 2033 | 45 | https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
SH1 | Coal | Estevan | 346 | 276 | 1992 | 1253.6232 | 2032 | 34 | https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
BD3 | Coal | Estevan | 228 | 120 | 1969/2014 | 1900 | 2034 |  | https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
CCS | Coal | Estevan | 254 |  | 2014 |  |  |  | https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
BD5 | Coal | Estevan | 189 | 139 | 1973 | 1359.7122 | 2035 | 53 | https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
BD4 | Coal | Estevan | 501 | 139 | 1970 | 3604.3165 | 2036 | 56 | https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
2537
Data from SaskPower response to the Saskatchewan Rate Review Panel March 13, 2026
https://saskratereview.ca/storage/593/01KKM0BHATXEX2B6X2G7V4121Q.pdf
Ontario Power Generation SMR | Nuclear SMR first unit | Ontario | 6000 | 300 |  | 20000 | https://www.world-nuclear-news.org/articles/what-is-the-budget-for-canadas-first-smr-project
Ontario Power Generation SMR | Nuclear SMR fourth unit | Ontario | 4100 | 300 |  | 13666.6667 | https://www.world-nuclear-news.org/articles/what-is-the-budget-for-canadas-first-smr-project
Ontario Power Generation SMR | Nuclear SMR whole project | Ontario | 21000 | 1200 |  | 17500 | https://www.world-nuclear-news.org/articles/what-is-the-budget-for-canadas-first-smr-project

## SaskPower AR data
| 2024-25 | 2023-24 | 2022-23 | 2021-22
Gas fuel cost ($M) | 316 | 366 | 449 | 397 |  | Sources:
Coal fuel cost ($M) | 313 | 296 | 318 | 280 |  | SaskPower Annual Report 2021-22
Imports ($M) | 173 | 178 | 163 | 81 |  | SaskPower Annual Report 2024-25
Wind ($M) | 108 | 84 | 93 | 63
Hydro ($M) | 18 | 16 | 20 | 18
Solar ($M) | 8 | 6 | 5 | 1
Electricity (GWh) | 2024-25 | 2023-24 | 2022-23 | 2021-22 | 2021-2024
Gas | 12426 | 11934 | 10575 | 10766 | 45701
Coal | 6245 | 7895 | 8424 | 9479 | 32043
Imports | 1929 | 2027 | 1806 | 752 | 6514
Wind | 2531 | 1981 | 2177 | 1661 | 8350
Hydro | 2769 | 2490 | 3244 | 2850 | 11353
Solar | 180 | 71 | 55 | 14 | 320
Fuel cost ($/MWh) | 2024-25 | 2023-24 | 2022-23 | 2021-22
Gas | 25.4305 | 30.6687 | 42.4586 | 36.8753
Coal | 50.1201 | 37.4921 | 37.7493 | 29.539
Imports | 89.6838 | 87.8145 | 90.2547 | 107.7128
Wind | 42.6709 | 42.4028 | 42.7193 | 37.929
Hydro | 6.5005 | 6.4257 | 6.1652 | 6.3158
Solar | 44.4444 | 84.507 | 90.9091 | 71.4286
Capacity (MW) | 2024-25 | 2023-24 | 2022-23 | 2021-22
Gas | 2434 | 2065 | 2160 | 2160
Coal | 1389 | 1389 | 1389 | 1389
Imports
Wind | 818 | 617 | 617 | 626
Hydro | 1153 | 1155 | 1154 | 989
Solar | 103 | 95 | 83 | 54
Capacity Factor (%) | 2024-25 | 2023-24 | 2022-23 | 2021-22
Gas | 58.28% | 65.97% | 55.89% | 56.9%
Coal | 51.32% | 64.89% | 69.23% | 77.9%
Imports
Wind | 35.32% | 36.65% | 40.28% | 30.29%
Hydro | 27.42% | 24.61% | 32.09% | 32.9%
Solar | 19.95% | 8.532% | 7.565% | 2.96%
CO2 (Annual) | 2024 | 2023 | 2022 | 2021 | 2021-2024
Coal | 7413974.021 | 8514775.705 | 9180474.626 | 10180186.011 | 35289410.363
Gas | 5423493.4033 | 5110627.3804 | 4573010.7255 | 4751508.7793 | 19858640.2884
Total | 12837467.4243 | 13625403.0854 | 13753485.3515 | 14931694.7903 | 55148050.6514
Approximate GHG intensity
Coal | 1187.1856 | 1078.5023 | 1089.7999 | 1073.9726 | 1101.3142
Gas | 436.4633 | 428.2409 | 432.436 | 441.3439 | 434.534
Gas /Coal intensity | 36.76% | 39.71% | 39.68% | 41.09% | 39.46%

## EIA AEO 2026 costs
Technology | First available year | Size (MW) | Lead time (years) | Base overnight cost ($2025/kW) | Technological optimism factor | Total overnight cost (2025$/kW) | Variable O&M (2025$/ MWh) | Fixed O&M (2025$/ kWy) | Heat rate (Btu/kWh)
Combustion turbine - single-shaft | 2028 | 627 | 3 | 1086 | 1 | 1086 | 3.49 | 16.23 | 6226
Combustion turbine - industrial frame | 2027 | 419 | 2 | 1158 | 1 | 1158 | 4.17 | 7.18 | 9142
Nuclear - light water reactor | 2031 | 2156 | 6 | 7862 | 1.05 | 8255 | 2.62 | 163.4 | 10445
Nuclear - small modular reactor | 2031 | 480 | 6 | 8937 | 1.1 | 9831 | 3.32 | 127.62 | 10445
Wind | 2028 | 200 | 3 | 1502 | 1 | 1712 | 0 | 34.57 | 3412 | 1712
Solar PV with tracking | 2027 | 150 | 2 | 1396 | 1 | 1484 | 0 | 23.6 | 3412 | 1484
USD to CAD Exchange Rate | 1.3751 | Exchange rate in April 2026: https://www.bankofcanada.ca/rates/exchange/monthly-exchange-rates/
Technology | First available year | Size (MW) | Lead time (years) | Base overnight cost ($2025/kW) | Technological optimism factor | Total overnight cost (2025$/kW) | Variable O&M (2025$/ MWh) | Fixed O&M (2025$/ kWy) | Heat rate (Btu/kWh)
Combustion turbine - single-shaft | 2028 | 627 | 3 | 1493.3586 | 1 | 1493.3586 | 4.7991 | 22.3179 | 6226
Combustion turbine - industrial frame | 2027 | 419 | 2 | 1592.3658 | 1 | 1592.3658 | 5.7342 | 9.8732 | 9142
Nuclear - light water reactor | 2031 | 2156 | 6 | 10811.0362 | 1.05 | 11351.4505 | 3.6028 | 224.6913 | 10445
Nuclear - small modular reactor | 2031 | 480 | 6 | 12289.2687 | 1.1 | 13518.6081 | 4.5653 | 175.4903 | 10445
Wind | 2028 | 200 | 3 | 2065.4002 | 1 | 2354.1712 | 0 | 47.5372 | 3412
Solar PV with tracking | 2027 | 150 | 2 | 1919.6396 | 1 | 2040.6484 | 0 | 32.4524 | 3412

## Gas efficiency
| Combined-cycle | Combustion turbine
Btu/kWh | 6226 | 9447
btu in 1 kwh | 3412 | 3412
Efficiency | 54.8% | 36.12%
Source:
https://www.eia.gov/outlooks/aeo/assumptions/pdf/EMM_Assumptions.pdf

## Carbon price exposure
Year | Carbon price | OBPS allowance on coal | Coal emissions intensity | Coal emissions (Mt) | Priced emissions | Cost ($M) | Inflation rate | Cost ($M) ($2026) | Year | OBPS allowance on gas | Gas emissions intensity (S1 & S2) | Scenario 2 & 3 emissions (Mt) | Priced emissions | Cost ($M) | Inflation rate | Cost ($M) ($2026) | OBPS allowance on gas | Gas emissions intensity (S3) | Scenario 4 emissions (Mt) | Priced emissions | Cost ($M) | Inflation rate | Cost ($M) ($2026)
2026 | 95 | 482 | 1080 | 12.3842 | 55.37% | 651.4312 | 2% | 651.4312 | 2026 | 164 | 324.0506 | 2.1829 | 49.39% | 102.4263 | 2% | 102.4263 | 164 | 499.5781 | 2.5776 | 67.17% | 164.4889 | 2% | 164.4889
2027 | 100 | 454 | 1080 | 12.3842 | 57.96% | 717.8242 | 2% | 703.7492 | 2027 | 123 | 324.0506 | 2.1829 | 62.04% | 135.4366 | 2% | 132.7809 | 123 | 499.5781 | 2.5776 | 75.38% | 194.3007 | 2% | 190.4909
2028 | 100 | 426 | 1080 | 12.3842 | 60.56% | 749.9313 | 2% | 720.8106 | 2028 | 82 | 324.0506 | 2.1829 | 74.7% | 163.056 | 2% | 156.7243 | 82 | 499.5781 | 2.5776 | 83.59% | 215.4552 | 2% | 207.0889
2029 | 100 | 398 | 1080 | 12.3842 | 63.15% | 782.0385 | 2% | 736.9323 | 2029 | 41 | 324.0506 | 2.1829 | 87.35% | 190.6754 | 2% | 179.6777 | 41 | 499.5781 | 2.5776 | 91.79% | 236.6098 | 2% | 222.9627
2030 | 115 | 370 | 1080 | 12.3842 | 65.74% | 936.2675 | 2% | 864.9664 | 2030 | 0 | 324.0506 | 2.1829 | 100% | 251.039 | 2% | 231.9212 | 0 | 499.5781 | 2.5776 | 100% | 296.4289 | 2% | 273.8545
2031 | 118 | 370 | 1080 | 12.3842 | 65.74% | 960.6919 | 2% | 870.1282 | 2031 | 0 | 324.0506 | 2.1829 | 100% | 257.5878 | 2% | 233.3052 | 0 | 499.5781 | 2.5776 | 100% | 304.1619 | 2% | 275.4888
2032 | 121 | 370 | 1080 | 12.3842 | 65.74% | 985.1162 | 2% | 874.755 | 2032 | 0 | 324.0506 | 2.1829 | 100% | 264.1367 | 2% | 234.5458 | 0 | 499.5781 | 2.5776 | 100% | 311.8948 | 2% | 276.9537
2033 | 124 | 370 | 1080 | 12.3842 | 65.74% | 1009.5406 | 2% | 878.8658 | 2033 | 0 | 324.0506 | 2.1829 | 100% | 270.6855 | 2% | 235.648 | 0 | 499.5781 | 2.5776 | 100% | 319.6277 | 2% | 278.2552
2034 | 127 | 370 | 1080 | 12.3842 | 65.74% | 1033.965 | 2% | 882.4791 | 2034 | 0 | 324.0506 | 2.1829 | 100% | 277.2344 | 2% | 236.6168 | 0 | 499.5781 | 2.5776 | 100% | 327.3607 | 2% | 279.3992
2035 | 130 | 370 | 1080 | 12.3842 | 65.74% | 1058.3893 | 2% | 885.6128 | 2035 | 0 | 324.0506 | 2.1829 | 100% | 283.7832 | 2% | 237.4571 | 0 | 499.5781 | 2.5776 | 100% | 335.0936 | 2% | 280.3913
2036 | 131.95 | 370 | 1080 | 12.3842 | 65.74% | 1074.2652 | 2% | 881.2716 | 2036 | 0 | 324.0506 | 2.1829 | 100% | 288.0399 | 2% | 236.2931 | 0 | 499.5781 | 2.5776 | 100% | 340.12 | 2% | 279.0169
2037 | 133.9292 | 370 | 1080 | 12.3842 | 65.74% | 1090.3791 | 2% | 876.9516 | 2037 | 0 | 324.0506 | 2.1829 | 100% | 292.3605 | 2% | 235.1348 | 0 | 499.5781 | 2.5776 | 100% | 345.2218 | 2% | 277.6491
2038 | 135.9382 | 370 | 1080 | 12.3842 | 65.74% | 1106.7348 | 2% | 872.6529 | 2038 | 0 | 324.0506 | 2.1829 | 100% | 296.7459 | 2% | 233.9822 | 0 | 499.5781 | 2.5776 | 100% | 350.4001 | 2% | 276.2881
2039 | 137.9773 | 370 | 1080 | 12.3842 | 65.74% | 1123.3359 | 2% | 868.3752 | 2039 | 0 | 324.0506 | 2.1829 | 100% | 301.1971 | 2% | 232.8352 | 0 | 499.5781 | 2.5776 | 100% | 355.6561 | 2% | 274.9337
2040 | 140.0469 | 370 | 1080 | 12.3842 | 65.74% | 1140.1859 | 2% | 864.1184 | 2040 | 0 | 324.0506 | 2.1829 | 100% | 305.7151 | 2% | 231.6938 | 0 | 499.5781 | 2.5776 | 100% | 360.991 | 2% | 273.586
2041 | 142.1476 | 370 | 1080 | 12.3842 | 65.74% | 1157.2887 | 2% | 859.8825 | 2041 | 0 | 324.0506 | 2.1829 | 100% | 310.3008 | 2% | 230.5581 | 0 | 499.5781 | 2.5776 | 100% | 366.4058 | 2% | 272.2449
2042 | 144.2798 | 370 | 1080 | 12.3842 | 65.74% | 1174.648 | 2% | 855.6674 | 2042 | 0 | 324.0506 | 2.1829 | 100% | 314.9553 | 2% | 229.4279 | 0 | 499.5781 | 2.5776 | 100% | 371.9019 | 2% | 270.9104
2043 | 146.444 | 370 | 1080 | 12.3842 | 65.74% | 1192.2677 | 2% | 851.473 | 2043 | 0 | 324.0506 | 2.1829 | 100% | 319.6797 | 2% | 228.3032 | 0 | 499.5781 | 2.5776 | 100% | 377.4804 | 2% | 269.5824
2044 | 148.6407 | 370 | 1080 | 12.3842 | 65.74% | 1210.1518 | 2% | 847.2991 | 2044 | 0 | 324.0506 | 2.1829 | 100% | 324.4749 | 2% | 227.1841 | 0 | 499.5781 | 2.5776 | 100% | 383.1426 | 2% | 268.2609
2045 | 150.8703 | 370 | 1080 | 12.3842 | 65.74% | 1228.304 | 2% | 843.1457 | 2045 | 0 | 324.0506 | 2.1829 | 100% | 329.342 | 2% | 226.0705 | 0 | 499.5781 | 2.5776 | 100% | 388.8898 | 2% | 266.9459
2046 | 153.1334 | 370 | 1080 | 12.3842 | 65.74% | 1246.7286 | 2% | 839.0126 | 2046 | 0 | 324.0506 | 2.1829 | 100% | 334.2821 | 2% | 224.9623 | 0 | 499.5781 | 2.5776 | 100% | 394.7231 | 2% | 265.6374
2047 | 155.4304 | 370 | 1080 | 12.3842 | 65.74% | 1265.4295 | 2% | 834.8998 | 2047 | 0 | 324.0506 | 2.1829 | 100% | 339.2963 | 2% | 223.8595 | 0 | 499.5781 | 2.5776 | 100% | 400.644 | 2% | 264.3352
2048 | 157.7618 | 370 | 1080 | 12.3842 | 65.74% | 1284.411 | 2% | 830.8071 | 2048 | 0 | 324.0506 | 2.1829 | 100% | 344.3858 | 2% | 222.7622 | 0 | 499.5781 | 2.5776 | 100% | 406.6536 | 2% | 263.0394
2049 | 160.1282 | 370 | 1080 | 12.3842 | 65.74% | 1303.6771 | 2% | 826.7346 | 2049 | 0 | 324.0506 | 2.1829 | 100% | 349.5516 | 2% | 221.6702 | 0 | 499.5781 | 2.5776 | 100% | 412.7534 | 2% | 261.75
2050 | 162.5302 | 370 | 1080 | 12.3842 | 65.74% | 1323.2323 | 2% | 822.6819 | 2050 | 0 | 324.0506 | 2.1829 | 100% | 354.7948 | 2% | 220.5836 | 0 | 499.5781 | 2.5776 | 100% | 418.9447 | 2% | 260.4669
|  |  |  | 309.6047 | Mt CO2e | 26806.2353 | $Million | 20844.7042 |  |  |  | 54.5737 | Mt CO2e | 7001.1827 | $Million | 5406.424 | $Million |  | 64.4411 | Mt CO2e | 8379.3506 | $Million | 6494.0213
[6 empty] | 26.8062 | $Billion | 20.8447 | [5 empty] | 7.0012 | $Billion | 5.4064 | $Billion |  |  |  | 8.3794 | $Billion | 6.494
Carbon pricing schedule: https://www.canada.ca/en/environment-climate-change/services/climate-change/pricing-pollution-how-it-will-work/carbon-pollution-pricing-federal-benchmark-information.html | [8 empty] | Carbon pricing schedule: https://www.canada.ca/en/environment-climate-change/services/climate-change/pricing-pollution-how-it-will-work/carbon-pollution-pricing-federal-benchmark-information.html
Coal-fired emissions allowance from Output-Based Pricing System Regulations, SOR/2019-266. | [8 empty] | Coal-fired emissions allowance from Output-Based Pricing System Regulations, SOR/2019-266.
Year | Carbon price | OBPS allowance on coal | Coal emissions intensity | Coal emissions (Mt) | Priced emissions | Cost ($M) | Inflation rate | Cost ($M) ($2026)
2026 | 95 | 482 | 1080 | 12.3842 | 55.37% | 651.4312 | 2% | 651.4312
2027 | 100 | 454 | 1080 | 12.3842 | 57.96% | 717.8242 | 2% | 703.7492
2028 | 100 | 426 | 1080 | 12.3842 | 60.56% | 749.9313 | 2% | 720.8106
2029 | 100 | 398 | 1080 | 12.3842 | 63.15% | 782.0385 | 2% | 736.9323
2030 | 115 | 370 | 1080 | 12.3842 | 65.74% | 936.2675 | 2% | 864.9664
2031 | 118 |  | 1080 | 12.3842 | 100% | 1461.3341 | 2% | 1323.5753
2032 | 121 |  | 1080 | 12.3842 | 100% | 1498.4867 | 2% | 1330.6133
2033 | 124 |  | 1080 | 12.3842 | 100% | 1535.6392 | 2% | 1336.8663
2034 | 127 |  | 1080 | 12.3842 | 100% | 1572.7918 | 2% | 1342.3626
2035 | 130 |  | 1080 | 12.3842 | 100% | 1609.9443 | 2% | 1347.1294
2036 | 131.95 |  | 1080 | 12.3842 | 100% | 1634.0935 | 2% | 1340.5258
2037 | 133.9292 |  | 1080 | 12.3842 | 100% | 1658.6049 | 2% | 1333.9546
2038 | 135.9382 |  | 1080 | 12.3842 | 100% | 1683.484 | 2% | 1327.4156
2039 | 137.9773 |  | 1080 | 12.3842 | 100% | 1708.7362 | 2% | 1320.9087
2040 | 140.0469 |  | 1080 | 12.3842 | 100% | 1734.3673 | 2% | 1314.4336
2041 | 142.1476 |  | 1080 | 12.3842 | 100% | 1760.3828 | 2% | 1307.9903
2042 | 144.2798 |  | 1080 | 12.3842 | 100% | 1786.7885 | 2% | 1301.5786
2043 | 146.444 |  | 1080 | 12.3842 | 100% | 1813.5904 | 2% | 1295.1983
2044 | 148.6407 |  | 1080 | 12.3842 | 100% | 1840.7942 | 2% | 1288.8493
2045 | 150.8703 |  | 1080 | 12.3842 | 100% | 1868.4061 | 2% | 1282.5314
2046 | 153.1334 |  | 1080 | 12.3842 | 100% | 1896.4322 | 2% | 1276.2445
2047 | 155.4304 |  | 1080 | 12.3842 | 100% | 1924.8787 | 2% | 1269.9884
2048 | 157.7618 |  | 1080 | 12.3842 | 100% | 1953.7519 | 2% | 1263.763
2049 | 160.1282 |  | 1080 | 12.3842 | 100% | 1983.0582 | 2% | 1257.5681
|  |  |  | 297.2205 | Mt CO2e | 36763.0576 | $Million | 28539.3872
[6 empty] | 36.7631 | $Billion | 28.5394

## Coal emissions intensity
Location of coal | Statistic | 2023 | 2024 | 2025 | 2026 | 2027 |  |  | Lignite coal SK | 1463 | kg CO2/tonne | https://data-donnees.az.ec.gc.ca/api/file?path=%2Fsubstances%2Fmonitor%2Fcanada-s-official-greenhouse-gas-inventory%2FD-Emission-Factors%2FEN_Annex6_Emission_Factors.pdf
Coronach | Heat value (MJ/tonne) | 13558 | 13880 | 13645 | 13470 | 13470
Coronach | Efficiency | 30% | 30% | 30% | 30% | 30%
Coronach | MJ required/GWh | 12000000 | 12000000 | 12000000 | 12000000 | 12000000
Coronach | Coal required (tonnes)/GWh | 885.0863 | 864.5533 | 879.443 | 890.8686 | 890.8686
Coronach | GHG intensity CO2 tonnes/GWh | 1294.8813 | 1264.8415 | 1286.6251 | 1303.3408 | 1303.3408
Estevan | Heat value (MJ/tonne) | 16303 | 16273 | 16213 | 16200 | 16200
Estevan | Efficiency | 30% | 30% | 30% | 30% | 30%
Estevan | MJ required/GWh | 12000000 | 12000000 | 12000000 | 12000000 | 12000000
Estevan | Coal required (tonnes)/GWh | 736.0608 | 737.4178 | 740.1468 | 740.7407 | 740.7407
Estevan | GHG intensity CO2 tonnes/GWh | 1076.857 | 1078.8423 | 1082.8348 | 1083.7037 | 1083.7037
Heat values from SaskPower's response to the Rate Review Panel
Efficiency assumed is typical for older sub-critical coal-fired power plant
Year | 2015 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
Coal emissions (kt CO2e) | 12546.356 | 11389.512 | 8710.114 | 11102.941 | 9843.442 | 9167.796 | 7544.989
Coal generation (GWh) | 12088.419 | 10035.4 | 7890.243 | 9650.353 | 8537.564 | 7934.855 | 7045.677
Coal emissions intensity (Mt CO2e/GWh) | 1037.8823 | 1134.9335 | 1103.9095 | 1150.5217 | 1152.9567 | 1155.3829 | 1070.8679 | 1126.7277
Gas emissions (kt CO2e) | 3615.462 | 4598.078 | 5172.652 | 4968.916 | 4948.817 | 5423.607 | 5639.033
Gas generation (GWh) | 6992.16 | 9270.356 | 10892.209 | 10844.793 | 10384.649 | 11650.075 | 12537.527
Gas emissions intensity (Mt CO2e/GWh) | 517.0737 | 495.998 | 474.8947 | 458.1845 | 476.5512 | 465.5427 | 449.7724
Data from Table A7-9 from the National Inventory Report (NIR) published by Environment and Climate Change Canada (ECCC)
https://data-donnees.az.ec.gc.ca/api/file?path=%2Fsubstances%2Fmonitor%2Fcanada-s-official-greenhouse-gas-inventory%2FC-Tables-Electricity-Canada-Provinces-Territories%2FEN_Annex7_Electricity_Intensity.xlsx

## Table A7–9
Table A7–9 | Electricity Generation and GHG Emission Details for Saskatchewan
|  | 1990 | 2005 | 2010 | 2015 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024a
Greenhouse Gas Emissionsb
kt CO2 equivalent
| Combustion | 11119.857 | 15264.055 | 16193.823 | 16170.939 | 15993.391 | 13887.461 | 16077.382 | 14803.869 | 14600.801 | 13192.866
| Coal | x | x | x | 12546.356 | 11389.512 | 8710.114 | 11102.941 | 9843.442 | 9167.796 | 7544.989
| Natural Gas | x | x | x | 3615.462 | 4598.078 | 5172.652 | 4968.916 | 4948.817 | 5423.607 | 5639.033
| Other Fuelsc | 6.469 | 4.302 | 11.61 | 9.121 | 5.801 | 4.695 | 5.525 | 11.61 | 9.397 | 8.844
| Other Emissionsd | 0 | 17.597 | 29.869 | 39.362 | 40.519 | 34.962 | 37.509 | 34.962 | 32.416 | 34.731
| Overall Totale,f,g | 11119.857 | 15281.652 | 16223.692 | 16210.301 | 16033.91 | 13922.424 | 16114.891 | 14838.832 | 14633.216 | 13227.597
Electricity Generationh,i
GWh
| Combustionj | 9660.252 | 14795.617 | 15141.096 | 19080.987 | 19305.957 | 18782.733 | 20495.316 | 18922.392 | 19585.128 | 19583.393
| Coal | 9343.206 | 12170.798 | 12084.243 | 12088.419 | 10035.4 | 7890.243 | 9650.353 | 8537.564 | 7934.855 | 7045.677
| Natural Gas | 308.269 | 2612.793 | 3039.168 | 6992.16 | 9270.356 | 10892.209 | 10844.793 | 10384.649 | 11650.075 | 12537.527
| Other Fuels | 8.777 | 12.026 | 17.685 | 0.408 | 0.201 | 0.281 | 0.17 | 0.179 | 0.198 | 0.189
| Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 4214.995 | 4572.91 | 3866.048 | 3425.611 | 3666.114 | 4423.24 | 2982.414 | 3304.033 | 2770.316 | 2453.241
| Other Renewablesk | 0 | 91.916 | 506.587 | 619.832 | 706.807 | 743.135 | 894.258 | 1789.982 | 1978.142 | 2143.34
| Other Generationl,m | 0 | 0 | 627.6 | 0 | 216.004 | 177.667 | 214.586 | 172.234 | 249.136 | 233.103
| Overall Totalf | 13875.247 | 19460.443 | 20141.331 | 23126.43 | 23894.882 | 24126.775 | 24586.574 | 24188.641 | 24582.722 | 24413.077
Greenhouse Gas Intensityn
Generation Intensity (g GHG / kWh electricity generated)
| CO2 intensity (g CO2 / kWh) | 796.357 | 779.781 | 799.767 | 695.279 | 665.252 | 571.673 | 649.732 | 607.923 | 589.713 | 536.518
| CH4 intensity (g CH4 / kWh) | 0.015 | 0.031 | 0.035 | 0.049 | 0.056 | 0.06 | 0.058 | 0.058 | 0.062 | 0.063
| N2O intensity (g N2O / kWh) | 0.018 | 0.017 | 0.018 | 0.016 | 0.016 | 0.014 | 0.015 | 0.015 | 0.014 | 0.013
| Generation Intensity (g CO2 eq / kWh)f | 801.431 | 785.285 | 805.506 | 700.956 | 671.015 | 577.047 | 655.423 | 613.454 | 595.258 | 541.826
Losses
| Unallocated Energy (GWh)o,p | 1333.055 | 1355.934 | 1840.918 | 1971.334 | 1629.392 | 1695.358 | 1581.004 | 1533.56 | 1418.423 | 1633.235
| SF6 Emissions (kt CO2 eq)q | 1.82 | 1.293 | 1.382 | 0.748 | 0.501 | 0.476 | 0.941 | 0.602 | 0.594 | 1.113
Consumption Intensity (g GHG / kWh electricity consumed)
| Consumption Intensity (g CO2 eq / kWh)r | 886.741 | 844.151 | 886.596 | 766.295 | 720.146 | 620.687 | 700.519 | 655.016 | 631.74 | 580.72
Notes:
Data presented include emissions, generation and intensity for facilities classified under NAICS code 22111 - Electric Power Generation.
a. Preliminary data.
b. Emissions based on data taken from the Report on Energy Supply-Demand in Canada, Catalogue No. 57-003-XIB, Statistics Canada.
c. Includes GHG emissions from the combustion of refined petroleum products (light fuel oil, heavy fuel oil, and diesel), petroleum coke,
still gas and other fuels not easily categorized.
d. GHG emissions from on-site combustion of fuel not directly related to electricity generation.
e. GHG emissions from the flooding of land for hydro dams are not included.
f. Totals may not add up to overall total due to rounding.
g. CO2 from carbon capture and storage has been removed from the total.
h. Taken from StatCan Data Tables 25-10-0019-01 (2005-2019), 25-10-0084-01 (2020-2024), and 25-10-0020-01 (2005-2024).
i. Taken from the Electric Power Generation, Transmission and Distribution (EPGTD) publication, Catalogue No. 57-202-XIB, Statistics Canada (for 1990-2004).
j. From 2014 onward, this includes most of the electricity generated from the by-product steam associated with the fuel combustion. Prior to 2014, it was not possible
to break this data into the original fuel source, so it was included in Other Generation.
k. Other Renewables - includes electricity generation by wind, tidal and solar.
l. NAICS category 221119, Other Electric Power Generation.
m. Prior to 2014, this includes electricity generation from steam from waste heat. From 2014 onward, most of the electricity generation from steam from waste heat is reported
as part of its original fuel source.
n. Intensity values have been rounded to reflect the estimated level of accuracy.
o. Adapted from StatCan Data Table 25-10-0021-001 (2005-2024), Cat. No. 57-202-XIB (1990-2004) or regional electricity system operators.
p. Includes transmission line losses, metering differences and other losses.
q. The electric utility sector's share of emissions from electrical equipment from CRT Category 2.F.viii (Production and Consumption of Halocarbons and SF6).
r. Consumption intensity values are impacted by unallocated energy and SF6 transmission emissions.
– Indicates no emissions or no electricity generation
x Indicates data not shown due to statistical limitations
Data from Table A7-9 from the National Inventory Report (NIR) published by Environment and Climate Change Canada (ECCC)
https://data-donnees.az.ec.gc.ca/api/file?path=%2Fsubstances%2Fmonitor%2Fcanada-s-official-greenhouse-gas-inventory%2FC-Tables-Electricity-Canada-Provinces-Territories%2FEN_Annex7_Electricity_Intensity.xlsx

## GHGRP data
Year | Coal | Gas | Total
2004 | 13198500 | 1891316.7351 | 15089816.7351
2005 | 12705765.698 | 1742095.9515 | 14447861.6495
2006 | 12341537.099 | 1822219.416 | 14163756.515
2007 | 13014863.601 | 1794629.9187 | 14809493.5197
2008 | 12881020.399 | 1944671.9808 | 14825692.3798
2009 | 13708321.2 | 1693259.0755 | 15401580.2755
2010 | 13392633.802 | 1906975.4326 | 15299609.2346
2011 | 12783544.1 | 2090288.7608 | 14873832.8608
2012 | 12962875.302 | 2549539.7899 | 15512415.0919
2013 | 11900034 | 3196644.7321 | 15096678.7321
2014 | 11708710.102 | 3288282.9678 | 14996993.0698
2015 | 11796036.999 | 3770876.6995 | 15566913.6985
2016 | 11241717.252 | 4058154.0445 | 15299871.2965
2017 | 11792302.8 | 4163138.1981 | 15955440.9981
2018 | 10987316.605 | 5099040.24 | 16086356.845
2019 | 10982478.414 | 4824341.2902 | 15806819.7042
2020 | 8151448.29 | 4603927.4036 | 12755375.6936
2021 | 10180186.011 | 4751508.7793 | 14931694.7903
2022 | 9180474.626 | 4573010.7255 | 13753485.3515
2023 | 8514775.705 | 5110627.3804 | 13625403.0854
2024 | 7413974.021 | 5423493.4033 | 12837467.4243
Emissions compiled from GHGRP with Saskatchewan electricity facilities coded as either fueled by coal or natural gas
https://data-donnees.az.ec.gc.ca/api/file?path=%2Fsubstances%2Fmonitor%2Fgreenhouse-gas-reporting-program-ghgrp-facility-greenhouse-gas-ghg-data%2FPDGES-GHGRP-GHGEmissionsGES-2004-Present.csv